## PMS(input)
JCM_ET_F_PMS_ver01.0（案3）
JCM Proposed Methodology Spreadsheet Form (input sheet) [Attachment to Proposed Methodology Form]
Table 1: Parameters to be monitored ex post
| (a) | (b) | (c) | (d) | (e) | (f) | (g) | (h) | (i) | (j)
| Monitoring point No. | Parameters | Description of data | Estimated Values | Units | Monitoring option | Source of data | Measurement methods and procedures | Monitoring frequency | Other comments
| 1 | PFCi,y | Project consumption of fossil fuel i of the applicable equipment in year y | 0 | kl, t, 1000Nm3/y | C | Project site activity. | On-site measurements will be carried out using fuel meters connected to the power generation units | Monthly
| 2 | RGPJ,y | Quantity of net electricity generation that is produced and fed into the grid as a result of the implementation of the JCM project activity in year y | 161184 | MWh/y | C | Electricity meters | Quantity of net electricity generation supplied by the project plant/unit to the grid in year y | Continuous measurement and at least monthly recording
| 3 | wsteam,CO2,y | average mass fraction of CO2 in the produced steam in year y | 0.01 | tCO2/ t steam | C | Meters | Non-condensable gases sampling is carried out at the steam field-power plant interface. Monitoring in production wells are not mandatory. The sampling of NCGs shall be in line with ASTM E1675-95a and same kind of the sampling method as the ASTME* | Quarterly | *Candidates of method: gas burette method, giggenbach bottle method Vacuum impinger method, Ozawa's method Two-hole syringe
| 4 | wsteam,CH4,y | average mass fraction of CH4 in the produced steam in year y | 5e-06 | tCH4/ t steam | C | Meters | Non-condensable gases sampling is carried out at the steam field-power plant interface. Monitoring in production wells are not mandatory. The sampling of NCGs shall be in line with ASTM E1675-95a and same kind of the sampling method as the ASTME* | Quarterly
| 5 | Msteam,y | Quantity of steam produced in year y | 2030918.4 | t steam/y | C | Project site activity. | Quantity of steam produced during the year in the production wells will be measured daily using a meter. Measurements will be recorded regularly in production reports. | Continuous measurement
| 6 | RF,OM,y | Operating margin CO2 emission factor for grid power plants and additional electricity to meet the minimum service level in year y calculated the latest emission factor (tbd). | 0 | tCO2/MWh | A | EEP | Operation margin CO2 emission factor for grid power plants and off-grid power plants. Net electricity generation by grid power plants is available at IEA/EEP. Estimated electricity generation by off-grid (conventional) power plants is available at the Ethiopian government (to be confirmed). | Annually
| 6 | EF,BT,y | Emission factor of power generation by the baseline technology to meet the supressed demand for electricity consumption: Kerosene | 0.0719 | tCO2/GJ* | A | IPCC* | Literature* | Annually
| 7 | EC,y | Electricity consumption per capita in year y | 60 | kWh/y | A | EIA or World Bank | Literature | Annually
*Dependent on the baseline technology. This table reflects the case of power generation by kerosene.
Table 2: Project-specific parameters to be fixed ex ante
| (a) | (b) |  | (c) | (d) | (e) |  |  | (f)
| Parameters | Description of data |  | Estimated Values | Units | Source of data |  |  | Other comments
| RF,BM,y | BM margin CO2 emission factor for grid power plants in year y |  | 0 | tCO2/MWh | EEP
Table3: Ex-ante estimation of CO2 emission reductions
| CO2 emission reductions |  | Units
| 49012 |  | tCO2/y
[Monitoring option]
| Option A | Based on public data which is measured by entities other than the project participants (Data used: publicly recognized data such as statistical data and specifications)
| Option B | Based on the amount of transaction which is measured directly using measuring equipments (Data used: commercial evidence such as invoices)
| Option C | Based on the actual measurement using measuring equipments (Data used: measured values)
III-9

## PMS(calc_process)
JCM_ET_F_PMS_ver01.0（案3）
JCM Proposed Methodology Spreadsheet Form (Calculation Process Sheet)
[Attachment to Proposed Methodology Form]
1. Calculations for emission reductions |  |  |  |  | Fuel type | Value | Units | Parameter
| Emission reductions during the period of year y |  |  |  |  | 49012.3472 | tCO2/y | ERy
2. Selected default values, etc.
|  | Global warming potential of methane valid for the relevant commitment period. |  |  |  | 21 | tCO2/tCH4 | GWPCH4
|  | CO2 emission factor of diesel in year y |  |  | Diesel | 0.0741 | tCO2/GJ
|  | Net calorific value of fossil fuel |  |  | Diesel | 37.7 | GJ/kl
|  | CO2 emission factor of fossil fuel power generation |  |  | Diesel | 0.8892 | tCO2/MWh
|  | Net calorific value of fossil fuel |  |  | Other Kerosene | 0 | GJ/kl
|  | CO2 emission factor of the baseline technology |  |  | Other Kerosene | 0.0719 | tCO2/GJ
|  | CO2 emission factor of the power generation by the baseline technology |  |  | Other Kerosene | 0.8628 | tCO2/MWh | EFBT,y
|  | Default efficiency factors for power plants |  |  | Oil | 0.3
|  | Electricity consumption per capita in year y |  |  |  | 60 | kWh/y | ECy
|  | Minimum service level of electricity consumption per capita |  |  |  | 120 | kWh/y | MSL
|  | OM CO2 emission factor for grid power plants |  |  |  | 0 | tCO2/ MWh | EFgrid,BM,y
|  | BM CO2 emission factor for grid power plants |  |  |  | 0 | tCO2/ MWh | EFgrid,CM,y
3. Calculations for reference emissions
| Reference emissions during the period of year y |  |  |  |  | 69534.7776 | tCO2/y | REy
|  | Quantity of net electricity generation that is produced and fed into the grid as a result of the implementation of the JCM project activity |  |  | - | 161184 | MWh/y | RGPJ,y
|  | Combined margin CO2 emission factor for grid power plants and additional electricity to meet the minimum service level in year y calculated the latest emission factor |  |  | - | 0.4314 | tCO2/ MWh | RF,CM,y
|  | Operating margin CO2 emission factor for grid power plants and additional electricity to meet the minimum service level in year y calculated the latest emission factor |  |  | - | 0.4314 | tCO2/ MWh | RF,OM,y
|  | Build margin CO2 emission factor for grid power plants and additional electricity to meet the minimum service level in year y calculated the latest emission factor |  |  | - | 0.4314 | tCO2/ MWh/ | RF,BM,y
|  | The weight of operating margin for calculating the combined margin |  |  | - | 0.5 | - | -
|  | The weights of build margin for calculating the combined margin |  |  | - | 0.5 | - | -
4. Calculations of the project emissions
| Project emissions during the period of year y |  |  |  |  | 20522.4304 | tCO2/y | PEy
|  | Project emissions from fossil fuel consumption in year y |  |  |  | 0 | tCO2/y | PEFF,y
|  |  | Project consumption of diesel of the applicable equipment in year y |  | Diesel | 0 | kl/y
|  |  | Net calorific value of fossil fuel |  | Diesel | 37.7 | GJ/kl
|  | Project emissions from the operation of geothermal power plants due to the release of NCGs in year y |  |  | - | 20522.4304 | tCO2/y | PEGP,y
|  |  | Average mass fraction of CO2 in the produced steam in year y |  | - | 1% | tCO2/t steam | wsteam,CO2,y
|  |  | Average mass fraction of CH4 in the produced steam in year y |  | - | 0.0005% | tCH4/t steam | wsteam,CH4,y
|  |  | Global warming potential of methane |  | - | 21 | tCO2/tCH4
|  |  | Quantity of steam produced in year y |  | - | 2030918.4 | t steam | Msteam,y
[List of Default Values]
|  |  |  | Net calorific value of fossil fuel NCVi,y | NCVi.y
[5 empty] | 37.7 | GJ/kl
|  |  |  | Other Kerosene |  | GJ/kl
MWh per GJ
|  |  |  | 1 MWh | 3.6 | GJ
CO2 emission factor of fossil fuel
|  |  |  | Diesel | 0.0741 | tCO2/GJ
|  |  |  | Other Kerosene | 0.0719 | tCO2/GJ
OM margin CO2 emission factor for grid power plants in year y
[5 empty] | 0 | tCO2/ MWh/
BM margin CO2 emission factor for grid power plants in year y
[5 empty] | 0 | tCO2/ MWh/
Global warming potential of methane
|  |  |  | CH4 | 21 | tCO2/tCH4
Default efficiency factors for power plants
|  |  |  | Oil | 30 | %
Global warming potential of methane
|  |  |  | MSL | 120 | kWh/y
III-10