## PMS(input)
JCM_MN_F_PMS_ver01.0
Joint Crediting Mechanism Proposed Methodology Spreadsheet Form (input sheet) [Attachment to Proposed Methodology Form]
(CHP3 high pressure unit)
Table 1: Parameters to be monitored ex post
| (a) | (b) | (c) |  | (d) | (e) | (f) | (g) | (h) | (i) | (j)
| Monitoring point No. | Parameters | Description of data |  | Estimated Values | Units | Monitoring option | Source of data | Measurement methods and procedures | Monitoring frequency | Other comments
|  | l(n)PJI | Length installed by the project thermal insulation material for main steam pipe No.n | n=1 | 127 | m | Option C | Installation drawing and site photographs after installation of the project thermal insulation material | Not applicable | Not applicable
|  |  |  | n=2 | 127 | m
|  |  |  | n=3 | 127 | m
|  |  |  | n=4 | 127 | m
|  |  |  | n=5 | 127 | m
|  |  |  | n=6 | 127 | m
|  |  |  | n=7 | 127 | m
|  |  |  | n=8 | 43 | m
|  |  |  | n=9 | 43 | m
|  |  |  | n=10 | 43 | m
|  |  |  | n=11 | 43 | m
|  |  |  | n=12 | 200 | m
|  | t(n)PJI | Thickness installeded by the project thermal insulation material for main steam pipe line No. n | n=1 | 20 | mm | Option C | The Product specification | Not applicable | Not applicable
|  |  |  | n=2 | 20 | mm
|  |  |  | n=3 | 20 | mm
|  |  |  | n=4 | 20 | mm
|  |  |  | n=5 | 20 | mm
|  |  |  | n=6 | 20 | mm
|  |  |  | n=7 | 20 | mm
|  |  |  | n=8 | 20 | mm
|  |  |  | n=9 | 20 | mm
|  |  |  | n=10 | 20 | mm
|  |  |  | n=11 | 20 | mm
|  |  |  | n=12 | 20 | mm
|  | SA(n)PJI-str,y | Total area where project thermal insulation materials have stripped on main steam pipe line No. n by the end of the year y | n=1 | 0 | m2 | Option C | Site photographs by the themal power plant | ·On the last day during each monitoring period, the person in charge does checking whethere physical damaged points are founded or not at all installation areas of the peoject thermal insulation and takes some electronic pictures .for evidences. ·Physical damaged areas are counted in conservative manner. | Daily
|  |  |  | n=2 | 0 | m2
|  |  |  | n=3 | 0 | m2
|  |  |  | n=4 | 0 | m2
|  |  |  | n=5 | 0 | m2
|  |  |  | n=6 | 0 | m2
|  |  |  | n=7 | 0 | m2
|  |  |  | n=8 | 0 | m2
|  |  |  | n=9 | 0 | m2
|  |  |  | n=10 | 0 | m2
|  |  |  | n=11 | 0 | m2
|  |  |  | n=12 | 0 | m2
|  | OH(n)sf,y | Steam flow hours in main steam pipe line No. n during the period of year y | n=1 | 4348 | hours | Option C | Plant record by the themal power plant (Daily recorded sheet) | [In case of boiler-common steam header line] Hourly data for steam flow, steam temperature and steam pressure in the main steam pipe at the boiler outlet is manually recorded in the control room. In case that hourly values for these parameters are recorded, the operation of on-off bulb of steam during the hour is regarded as on-status. In case that hourly values for these parameters are not recorded, the operation of on-off bulb of steam during the hour is regarded as off-status. [In case of common steam header-turbine line] The following parameters are manually recorded in the control room. ·Hourly data for electricity generated the generator linked the turbine ·Hourly data for steam flow rate, steam temperature and steam pressure in the main steam pipe at the turbine inlet This parameter is counted by one of above-mentioned two items. In case that hourly value for this parameter is recorded, the turbine operation (steam is fed to the turbine) during the hour is regarded as on-status. In case that hourly value for this parameter is not recorded, the turbine operation (steam is fed to the turbine) during the hour is regarded as on-status. [In case of common steam header line] In conservative manner, this value is counted by average steam flow hours on all common header-turbine steam lines. | Measuing frequency: Continuously Recording frequency: Hourly
|  |  |  | n=2 | 4348 | hours
|  |  |  | n=3 | 4348 | hours
|  |  |  | n=4 | 4348 | hours
|  |  |  | n=5 | 4348 | hours
|  |  |  | n=6 | 4348 | hours
|  |  |  | n=7 | 4348 | hours
|  |  |  | n=8 | 6070 | hours
|  |  |  | n=9 | 6070 | hours
|  |  |  | n=10 | 6070 | hours
|  |  |  | n=11 | 6070 | hours
|  |  |  | n=12 | 6070 | hours
|  | lPJI,0 | Thermal conductivity of new project thermal insulation material (before installation) |  | 0.25 | W/m･K | Option C | Measurement certification by authorized laboratory | According to testing data by the loboratory, thermal conductivity curve for temperature range between 50°C and 300°C shall be drawn. Average value of thermal conductivity for temperature range between 50°C and 300°C is applied to this parameter. | Once before installation of project insulation material
|  | lPJI,y | Thermal conductivity of used project thermal insulation material after y years later since installation |  | 0.275 | W/m･K | Option C | Measurement certification by authorized laboratory | ·3 sampling installation zones (200mm´200mm of project thermal insulation ´5partitions for each zone) of project thermal insulation material are eatablished, for the purpose of monitoring of this parameter. 3 sampling installation zones are chosen from central area on common steam header line, because amount of time for steam flow in the pipe around there is longest. ·On the last day during each monitoring period, project thermal insulation of 1 partition (200mm´200mm ) for each zone will be removed, and thermal conductivities of removed materials will be measured by thermal conductivity meter in authorized laboratory. Maximum value of removed materials for 3 partitions will be applied to this parameter. · Considering actual operation temperature, this parameter is identified by thermal conductivity at 250°C. | Once after each monitoring period
Table 2: Project-specific parameters to be fixed ex ante
| (a) | (b) |  |  | (c) | (d) | (e) |  |  | (f)
| Parameters | Description of data |  |  | Estimated Values | Units | Source of data |  |  | Other comments
| qRRE | Reference radiation heat quantity (before thermal insulation installation) from main steam pipe linage |  |  | 647 | W/m2 | According to the Feasibility Study in FY2014
| f(n)PJI-eff | Thermal insulation efficiency by the project thermal insulation material for main steam pipe line No. n |  | n=1 | 0.39 | Non-dimension | According to the Feasibility Study in FY2014
|  |  |  | n=2 | 0.39 | Non-dimension
|  |  |  | n=3 | 0.39 | Non-dimension
|  |  |  | n=4 | 0.39 | Non-dimension
|  |  |  | n=5 | 0.39 | Non-dimension
|  |  |  | n=6 | 0.39 | Non-dimension
|  |  |  | n=7 | 0.39 | Non-dimension
|  |  |  | n=8 | 0.39 | Non-dimension
|  |  |  | n=9 | 0.39 | Non-dimension
|  |  |  | n=10 | 0.39 | Non-dimension
|  |  |  | n=11 | 0.39 | Non-dimension
|  |  |  | n=12 | 0.39 | Non-dimension
| d(n)ExtP | Outside diameter of the existing pipe for main steam pipe line No. n |  | n=1,7 | 273 | mm | Drawing for design according to the thermal power plant
|  |  |  | n=8,11 | 159 | mm
|  |  |  | n=12 | 273 | mm
| t(n)ExtI | Thickness covered by the existing thermal insulation material on main steam pipe line No. n |  | n=1,12 | 150 | mm | Equipment specification according to the thermal power plant
Table3: Ex-ante estimation of CO2 emission reductions
| CO2 emission reductions |  | Units
| 761 |  | tCO2/y
[Monitoring option]
| Option A | Based on public data which is measured by entities other than the project participants (Data used: publicly recognized data such as statistical data and specifications)
| Option B | Based on the amount of transaction which is measured directly using measuring equipments (Data used: commercial evidence such as invoices)
| Option C | Based on the actual measurement using measuring equipments (Data used: measured values)

## PMS(calc_process)
JCM_MN_F_PMS_ver01.0
Joint Crediting Mechanism Proposed Methodology Spreadsheet Form (Calculation Process Sheet)
[Attachment to Proposed Methodology Form]
(CHP3 high pressure unit)
1. Calculations for emission reductions | [6 empty] | Fuel type | Value | Units | Parameter
| Emission reductions during the period of year y | [6 empty] | 761 | tCO2/y | ERy
2. Selected default values, etc.
| Boiler efficiency | [6 empty] | 1 | Non-dimension | hboiler
| CO2 Emission factor of coal | [6 empty] | 0.101 | tCO2/GJ | EFCO2,coal:
3. Calculations for reference emissions
| Reference emissions during the period of year y | [6 empty] | 2505 | tCO2/y | REy
|  | Reference emissions during the period of year y | [5 empty] | 2505 | tCO2/y | REy
|  |  | Boiler efficiency |  |  |  |  | 1 | Non-dimension | hboiler
|  |  | CO2 Emission factor of coal |  |  |  |  | 0.101 | tCO2/GJ | EFCO2,coal
|  |  | Total reference radiation quantity during the period of year y |  |  |  |  | 24803.7425 | GJ/y | QRRE,y
|  |  |  | Reference radiation quantity on main steam pipe line No. 1 during the period of year y |  |  |  | 2315.2854 | GJ/y | QR(1)RE,y
[5 empty] | Reference radiating surface area |  |  | 228.6168 | m2 | SA(1)RE,y
[6 empty] | Surface area covered by existing insulation material |  | 228.6168 | m2 | SA(1)ExtI
[6 empty] | Surface area covered by the project thermal insulation material |  | 244.5761 | m2 | SA(1)PJI-ins
[6 empty] | Total area where project thermal insulation materials have stripped |  | 0 | m2 | SA(1)PJI-str,y
[5 empty] | Reference radiation heat quantity |  |  | 647 | W/m2 | qRRE
[5 empty] | Steam flow hours |  |  | 4348 | hours | OH(1)sf,y
|  |  |  | Reference radiation quantity on main steam pipe line No. 2 during the period of year y |  |  |  | 2315.2854 | GJ/y | QR(2)RE,y
[5 empty] | Reference radiating surface area |  |  | 228.6168 | m2 | SA(2)RE,y
[6 empty] | Surface area covered by existing insulation material |  | 228.6168 | m2 | SA(2)ExtI
[6 empty] | Surface area covered by the project thermal insulation material |  | 244.5761 | m2 | SA(2)PJI-ins
[6 empty] | Total area where project thermal insulation materials have stripped |  | 0 | m2 | SA(2)PJI-str,y
[5 empty] | Reference radiation heat quantity |  |  | 647 | W/m2 | qRRE
[5 empty] | Steam flow hours |  |  | 4348 | hours | OH(2)sf,y
|  |  |  | Reference radiation quantity on main steam pipe line No. 3 during the period of year y |  |  |  | 2315.2854 | GJ/y | QR(3)RE,y
[5 empty] | Reference radiating surface area |  |  | 228.6168 | m2 | SA(3)RE,y
[6 empty] | Surface area covered by existing insulation material |  | 228.6168 | m2 | SA(3)ExtI
[6 empty] | Surface area covered by the project thermal insulation material |  | 244.5761 | m2 | SA(3)PJI-ins
[6 empty] | Total area where project thermal insulation materials have stripped |  | 0 | m2 | SA(3)PJI-str,y
[5 empty] | Reference radiation heat quantity |  |  | 647 | W/m2 | qRRE
[5 empty] | Steam flow hours |  |  | 4348 | hours | OH(3)sf,y
|  |  |  | Reference radiation quantity on main steam pipe line No. 4 during the period of year y |  |  |  | 2315.2854 | GJ/y | QR(4)RE,y
[5 empty] | Reference radiating surface area |  |  | 228.6168 | m2 | SA(4)RE,y
[6 empty] | Surface area covered by existing insulation material |  | 228.6168 | m2 | SA(4)ExtI
[6 empty] | Surface area covered by the project thermal insulation material |  | 244.5761 | m2 | SA(4)PJI-ins
[6 empty] | Total area where project thermal insulation materials have stripped |  | 0 | m2 | SA(4)PJI-str,y
[5 empty] | Reference radiation heat quantity |  |  | 647 | W/m2 | qRRE
[5 empty] | Steam flow hours |  |  | 4348 | hours | OH(4)sf,y
|  |  |  | Reference radiation quantity on main steam pipe line No. 5 during the period of year y |  |  |  | 2315.2854 | GJ/y | QR(5)RE,y
[5 empty] | Reference radiating surface area |  |  | 228.6168 | m2 | SA(5)RE,y
[6 empty] | Surface area covered by existing insulation material |  | 228.6168 | m2 | SA(5)ExtI
[6 empty] | Surface area covered by the project thermal insulation material |  | 244.5761 | m2 | SA(5)PJI-ins
[6 empty] | Total area where project thermal insulation materials have stripped |  | 0 | m2 | SA(5)PJI-str,y
[5 empty] | Reference radiation heat quantity |  |  | 647 | W/m2 | qRRE
[5 empty] | Steam flow hours |  |  | 4348 | hours | OH(5)sf,y
|  |  |  | Reference radiation quantity on main steam pipe line No. 6 during the period of year y |  |  |  | 2315.2854 | GJ/y | QR(6)RE,y
[5 empty] | Reference radiating surface area |  |  | 228.6168 | m2 | SA(6)RE,y
[6 empty] | Surface area covered by existing insulation material |  | 228.6168 | m2 | SA(6)ExtI
[6 empty] | Surface area covered by the project thermal insulation material |  | 244.5761 | m2 | SA(6)PJI-ins
[6 empty] | Total area where project thermal insulation materials have stripped |  | 0 | m2 | SA(6)PJI-str,y
[5 empty] | Reference specific radiation heat quantity |  |  | 647 | W/m2 | qRRE
[5 empty] | Steam flow hours |  |  | 4348 | hours | OH(6)sf,y
|  |  |  | Reference radiation quantity on main steam pipe line No. 7 during the period of year y |  |  |  | 2315.2854 | GJ/y | QR(7)RE,y
[5 empty] | Reference radiating surface area |  |  | 228.6168 | m2 | SA(7)RE,y
[6 empty] | Surface area covered by existing insulation material |  | 228.6168 | m2 | SA(7)ExtI
[6 empty] | Surface area covered by the project thermal insulation material |  | 244.5761 | m2 | SA(7)PJI-ins
[6 empty] | Total area where project thermal insulation materials have stripped |  | 0 | m2 | SA(7)PJI-str,y
[5 empty] | Reference radiation heat quantity |  |  | 647 | W/m2 | qRRE
[5 empty] | Steam flow hours |  |  | 4348 | hours | OH(7)sf,y
|  |  |  | Reference radiation quantity on main steam pipe line No. 8 during the period of year y |  |  |  | 876.6505 | GJ/y | QR(8)RE,y
[5 empty] | Reference radiating surface area |  |  | 62.0056 | m2 | SA(8)RE,y
[6 empty] | Surface area covered by existing insulation material |  | 62.0056 | m2 | SA(8)ExtI
[6 empty] | Surface area covered by the project thermal insulation material |  | 67.4092 | m2 | SA(8)PJI-ins
[6 empty] | Total area where project thermal insulation materials have stripped |  | 0 | m2 | SA(8)PJI-str,y
[5 empty] | Reference radiation heat quantity |  |  | 647 | W/m2 | qRRE
[5 empty] | Steam flow hours |  |  | 6070 | hours | OH(8)sf,y
|  |  |  | Reference radiation quantity on main steam pipe line No. 9 during the period of year y |  |  |  | 876.6505 | GJ/y | QR(9)RE,y
[5 empty] | Reference radiating surface area |  |  | 62.0056 | m2 | SA(9)RE,y
[6 empty] | Surface area covered by existing insulation material |  | 62.0056 | m2 | SA(9)ExtI
[6 empty] | Surface area covered by the project thermal insulation material |  | 67.4092 | m2 | SA(9)PJI-ins
[6 empty] | Total area where project thermal insulation materials have stripped |  | 0 | m2 | SA(9)PJI-str,y
[5 empty] | Reference radiation heat quantity |  |  | 647 | W/m2 | qRRE
[5 empty] | Steam flow hours |  |  | 6070 | hours | OH(9)sf,y
|  |  |  | Reference radiation quantity on main steam pipe line No. 10 during the period of year y |  |  |  | 876.6505 | GJ/y | QR(10)RE,y
[5 empty] | Reference radiating surface area |  |  | 62.0056 | m2 | SA(10)RE,y
[6 empty] | Surface area covered by existing insulation material |  | 62.0056 | m2 | SA(10)ExtI
[6 empty] | Surface area covered by the project thermal insulation material |  | 67.4092 | m2 | SA(10)PJI-ins
[6 empty] | Total area where project thermal insulation materials have stripped |  | 0 | m2 | SA(10)PJI-str,y
[5 empty] | Reference radiation heat quantity |  |  | 647 | W/m2 | qRRE
[5 empty] | Steam flow hours |  |  | 6070 | hours | OH(10)sf,y
|  |  |  | Reference radiation quantity on main steam pipe line No. 11 during the period of year y |  |  |  | 876.6505 | GJ/y | QR(11)RE,y
[5 empty] | Reference radiating surface area |  |  | 62.0056 | m2 | SA(11)RE,y
[6 empty] | Surface area covered by existing insulation material |  | 62.0056 | m2 | SA(11)ExtI
[6 empty] | Surface area covered by the project thermal insulation material |  | 67.4092 | m2 | SA(11)PJI-ins
[6 empty] | Total area where project thermal insulation materials have stripped |  | 0 | m2 | SA(11)PJI-str,y
[5 empty] | Reference radiation heat quantity |  |  | 647 | W/m2 | qRRE
[5 empty] | Steam flow hours |  |  | 6070 | hours | OH(11)sf,y
|  |  |  | Reference radiation quantity on main steam pipe line No. 12 during the period of year y |  |  |  | 5090.1428 | GJ/y | QR(12)RE,y
[5 empty] | Reference radiating surface area |  |  | 360.0265 | m2 | SA(12)RE,y
[6 empty] | Surface area covered by existing insulation material |  | 360.0265 | m2 | SA(12)ExtI
[6 empty] | Surface area covered by the project thermal insulation material |  | 385.1593 | m2 | SA(12)PJI-ins
[6 empty] | Total area where project thermal insulation materials have stripped |  | 0 | m2 | SA(12)PJI-str,y
[5 empty] | Reference radiation heat quantity |  |  | 647 | W/m2 | qRRE
[5 empty] | Steam flow hours |  |  | 6070 | hours | OH(12)sf,y
4. Calculations of the project emissions
| Project emissions during the period of year y | [6 empty] | 1744 | tCO2/y | PEy
|  | Project emissions during the period of year y | [5 empty] | 1744 | tCO2/y | PEy
|  |  | Boiler efficiency |  |  |  |  | 1 | Fraction | hboiler
|  |  | CO2 Emission factor of coal |  |  |  |  | 0.101 | tCO2/GJ | EFCO2,coal:
|  |  | Total project radiation quantity during the period of year y |  |  |  |  | 17264.8174 | GJ/y | QRPJ,y
|  |  |  | Project radiation quantity on main steam pipe line No. 1 during the period of year y |  |  |  | 1607.8865 | GJ/y | QR(1)PJ,y
[5 empty] | Project radiating surface area |  |  | 244.5761 | m2 | SA(1)PJ,y
[6 empty] | Surface area covered by project thermal insulation material |  | 244.5761 | m2 | SA(1)PJI-ins
[6 empty] | Total area where project thermal insulation materials have stripped |  | 0 | m2 | SA(1)PJI-str,y
[5 empty] | Project radiation heat quantity |  |  | 420 | W/m2 | qR(1)PJ,y
[6 empty] | Reference radiation heat quantity |  | 647 | W/m2 | qRRE
[6 empty] | Thermal insulation efficiency by the project thermal insulation material |  | 0.39 | Non-dimension | f(1)PJI-eff
[6 empty] | Decreasing rate of thermal insulation efficiency by the project thermal insulation material |  | 0.1 | Non-dimension | fPJI-dec,y
[5 empty] | Steam flow hours |  |  | 4348 | hours/y | OH(1)sf,y
|  |  |  | Project radiation quantity on main steam pipe line No. 2 during the period of year y |  |  |  | 1607.8865 | GJ/y | QR(2)PJ,y
[5 empty] | Project radiating surface area |  |  | 244.5761 | m2 | SA(2)PJ,y
[6 empty] | Surface area covered by project thermal insulation material |  | 244.5761 | m2 | SA(2)PJI-ins
[6 empty] | Total area where project thermal insulation materials have stripped |  | 0 | m2 | SA(2)PJI-str,y
[5 empty] | Project radiation heat quantity |  |  | 420 | W/m2 | qR(2)PJ,y
[6 empty] | Reference radiation heat quantity |  | 647 | W/m2 | qRRE
[6 empty] | Thermal insulation efficiency by the project thermal insulation material |  | 0.39 | Non-dimension | f(2)PJI-eff
[6 empty] | Decreasing rate of thermal insulation efficiency by the project thermal insulation material |  | 0.1 | Non-dimension | fPJI-dec,y
[5 empty] | Steam flow hours |  |  | 4348 | hours/y | OH(2)sf,y
|  |  |  | Project radiation quantity on main steam pipe line No. 3 during the period of year y |  |  |  | 1607.8865 | GJ/y | QR(3)PJ,y
[5 empty] | Project radiating surface area |  |  | 244.5761 | m2 | SA(3)PJ,y
[6 empty] | Surface area covered by project thermal insulation material |  | 244.5761 | m2 | SA(3)PJI-ins
[6 empty] | Total area where project thermal insulation materials have stripped |  | 0 | m2 | SA(3)PJI-str,y
[5 empty] | Project radiation heat quantity |  |  | 420 | W/m2 | qR(3)PJ,y
[6 empty] | Reference radiation heat quantity |  | 647 | W/m2 | qRRE
[6 empty] | Thermal insulation efficiency by the project thermal insulation material |  | 0.39 | Non-dimension | f(3)PJI-eff
[6 empty] | Decreasing rate of thermal insulation efficiency by the project thermal insulation material |  | 0.1 | Non-dimension | fPJI-dec,y
[5 empty] | Steam flow hours |  |  | 4348 | hours/y | OH(3)sf,y
|  |  |  | Project radiation quantity on main steam pipe line No. 4 during the period of year y |  |  |  | 1607.8865 | GJ/y | QR(4)PJ,y
[5 empty] | Project radiating surface area |  |  | 244.5761 | m2 | SA(4)PJ,y
[6 empty] | Surface area covered by project thermal insulation material |  | 244.5761 | m2 | SA(4)PJI-ins
[6 empty] | Total area where project thermal insulation materials have stripped |  | 0 | m2 | SA(4)PJI-str,y
[5 empty] | Project radiation heat quantity |  |  | 420 | W/m2 | qR(4)PJ,y
[6 empty] | Reference radiation heat quantity |  | 647 | W/m2 | qRRE
[6 empty] | Thermal insulation efficiency by the project thermal insulation material |  | 0.39 | Non-dimension | f(4)PJI-eff
[6 empty] | Decreasing rate of thermal insulation efficiency by the project thermal insulation material |  | 0.1 | Non-dimension | fPJI-dec,y
[5 empty] | Steam flow hours |  |  | 4348 | hours/y | OH(4)sf,y
|  |  |  | Project radiation quantity on main steam pipe line No. 5 during the period of year y |  |  |  | 1607.8865 | GJ/y | QR(5)PJ,y
[5 empty] | Project radiating surface area |  |  | 244.5761 | m2 | SA(5)PJ,y
[6 empty] | Surface area covered by project thermal insulation material |  | 244.5761 | m2 | SA(5)PJI-ins
[6 empty] | Total area where project thermal insulation materials have stripped |  | 0 | m2 | SA(5)PJI-str,y
[5 empty] | Project radiation heat quantity |  |  | 420 | W/m2 | qR(5)PJ,y
[6 empty] | Reference radiation heat quantity |  | 647 | W/m2 | qRRE
[6 empty] | Thermal insulation efficiency by the project thermal insulation material |  | 0.39 | Non-dimension | f(5)PJI-eff
[6 empty] | Decreasing rate of thermal insulation efficiency by the project thermal insulation material |  | 0.1 | Non-dimension | fPJI-dec,y
[5 empty] | Steam flow hours |  |  | 4348 | hours/y | OH(5)sf,y
|  |  |  | Project radiation quantity on main steam pipe line No. 6 during the period of year y |  |  |  | 1607.8865 | GJ/y | QR(6)PJ,y
[5 empty] | Project radiating surface area |  |  | 244.5761 | m2 | SA(6)PJ,y
[6 empty] | Surface area covered by project thermal insulation material |  | 244.5761 | m2 | SA(6)PJI-ins
[6 empty] | Total area where project thermal insulation materials have stripped |  | 0 | m2 | SA(6)PJI-str,y
[5 empty] | Project radiation heat quantity |  |  | 420 | W/m2 | qR(6)PJ,y
[6 empty] | Reference radiation heat quantity |  | 647 | W/m2 | qRRE
[6 empty] | Thermal insulation efficiency by the project thermal insulation material |  | 0.39 | Non-dimension | f(6)PJI-eff
[6 empty] | Decreasing rate of thermal insulation efficiency by the project thermal insulation material |  | 0.1 | Non-dimension | fPJI-dec,y
[5 empty] | Steam flow hours |  |  | 4348 | hours/y | OH(6)sf,y
|  |  |  | Project radiation quantity on main steam pipe line No. 7 during the period of year y |  |  |  | 1607.8865 | GJ/y | QR(7)PJ,y
[5 empty] | Project radiating surface area |  |  | 244.5761 | m2 | SA(7)PJ,y
[6 empty] | Surface area covered by project thermal insulation material |  | 244.5761 | m2 | SA(7)PJI-ins
[6 empty] | Total area where project thermal insulation materials have stripped |  | 0 | m2 | SA(7)PJI-str,y
[5 empty] | Project radiation heat quantity |  |  | 420 | W/m2 | qR(7)PJ,y
[6 empty] | Reference radiation heat quantity |  | 647 | W/m2 | qRRE
[6 empty] | Thermal insulation efficiency by the project thermal insulation material |  | 0.39 | Non-dimension | f(7)PJI-eff
[6 empty] | Decreasing rate of thermal insulation efficiency by the project thermal insulation material |  | 0.1 | Non-dimension | fPJI-dec,y
[5 empty] | Steam flow hours |  |  | 4348 | hours/y | OH(7)sf,y
|  |  |  | Project radiation quantity on main steam pipe line No. 8 during the period of year y |  |  |  | 618.6704 | GJ/y | QR(8)PJ,y
[5 empty] | Project radiating surface area |  |  | 67.4092 | m2 | SA(8)PJ,y
[6 empty] | Surface area covered by project thermal insulation material |  | 67.4092 | m2 | SA(8)PJI-ins
[6 empty] | Total area where project thermal insulation materials have stripped |  | 0 | m2 | SA(8)PJI-str,y
[5 empty] | Project radiation heat quantity |  |  | 420 | W/m2 | qR(8)PJ,y
[6 empty] | Reference radiation heat quantity |  | 647 | W/m2 | qRRE
[6 empty] | Thermal insulation efficiency by the project thermal insulation material |  | 0.39 | Non-dimension | f(8)PJI-eff
[6 empty] | Decreasing rate of thermal insulation efficiency by the project thermal insulation material |  | 0.1 | Non-dimension | fPJI-dec,y
[5 empty] | Steam flow hours |  |  | 6070 | hours/y | OH(8)sf,y
|  |  |  | Project radiation quantity on main steam pipe line No. 9 during the period of year y |  |  |  | 618.6704 | GJ/y | QR(9)PJ,y
[5 empty] | Project radiating surface area |  |  | 67.4092 | m2 | SA(9)PJ,y
[6 empty] | Surface area covered by project thermal insulation material |  | 67.4092 | m2 | SA(9)PJI-ins
[6 empty] | Total area where project thermal insulation materials have stripped |  | 0 | m2 | SA(9)PJI-str,y
[5 empty] | Project radiation heat quantity |  |  | 420 | W/m2 | qR(9)PJ,y
[6 empty] | Reference radiation heat quantity |  | 647 | W/m2 | qRRE
[6 empty] | Thermal insulation efficiency by the project thermal insulation material |  | 0.39 | Non-dimension | f(9)PJI-eff
[6 empty] | Decreasing rate of thermal insulation efficiency by the project thermal insulation material |  | 0.1 | Non-dimension | fPJI-dec,y
[5 empty] | Steam flow hours |  |  | 6070 | hours/y | OH(9)sf,y
|  |  |  | Project radiation quantity on main steam pipe line No. 10 during the period of year y |  |  |  | 618.6704 | GJ/y | QR(10)PJ,y
[5 empty] | Project radiating surface area |  |  | 67.4092 | m2 | SA(10)PJ,y
[6 empty] | Surface area covered by project thermal insulation material |  | 67.4092 | m2 | SA(10)PJI-ins
[6 empty] | Total area where project thermal insulation materials have stripped |  | 0 | m2 | SA(10)PJI-str,y
[5 empty] | Project radiation heat quantity |  |  | 420 | W/m2 | qR(10)PJ,y
[6 empty] | Reference radiation heat quantity |  | 647 | W/m2 | qRRE
[6 empty] | Thermal insulation efficiency by the project thermal insulation material |  | 0.39 | Non-dimension | f(10)PJI-eff
[6 empty] | Decreasing rate of thermal insulation efficiency by the project thermal insulation material |  | 0.1 | Non-dimension | fPJI-dec,y
[5 empty] | Steam flow hours |  |  | 6070 | hours/y | OH(10)sf,y
|  |  |  | Project radiation quantity on main steam pipe line No. 11 during the period of year y |  |  |  | 618.6704 | GJ/y | QR(11)PJ,y
[5 empty] | Project radiating surface area |  |  | 67.4092 | m2 | SA(11)PJ,y
[6 empty] | Surface area covered by project thermal insulation material |  | 67.4092 | m2 | SA(11)PJI-ins
[6 empty] | Total area where project thermal insulation materials have stripped |  | 0 | m2 | SA(11)PJI-str,y
[5 empty] | Project radiation heat quantity |  |  | 420 | W/m2 | qR(11)PJ,y
[6 empty] | Reference radiation heat quantity |  | 647 | W/m2 | qRRE
[6 empty] | Thermal insulation efficiency by the project thermal insulation material |  | 0.39 | Non-dimension | f(11)PJI-eff
[6 empty] | Decreasing rate of thermal insulation efficiency by the project thermal insulation material |  | 0.1 | Non-dimension | fPJI-dec,y
[5 empty] | Steam flow hours |  |  | 6070 | hours/y | OH(11)sf,y
|  |  |  | Project radiation quantity on main steam pipe line No. 12 during the period of year y |  |  |  | 3534.9301 | GJ/y | QR(12)PJ,y
[5 empty] | Project radiating surface area |  |  | 385.1593 | m2 | SA(12)PJ,y
[6 empty] | Surface area covered by project thermal insulation material |  | 385.1593 | m2 | SA(12)PJI-ins
[6 empty] | Total area where project thermal insulation materials have stripped |  | 0 | m2 | SA(12)PJI-str,y
[5 empty] | Project radiation heat quantity |  |  | 420 | W/m2 | qR(12)PJ,y
[6 empty] | Reference radiation heat quantity |  | 647 | W/m2 | qRRE
[6 empty] | Thermal insulation efficiency by the project thermal insulation material |  | 0.39 | Non-dimension | f(12)PJI-eff
[6 empty] | Decreasing rate of thermal insulation efficiency by the project thermal insulation material |  | 0.1 | Non-dimension | fPJI-dec,y
[5 empty] | Steam flow hours |  |  | 6070 | hours/y | OH(12)sf,y
[List of Default Values]
[6 empty] | CO2 Emission factor of coal (EFCO2,coal) | 0.101 | tCO2/GJ
[6 empty] | Boiler efficiency (hboiler) | 1 | Non-dimension

## CHP3 HP unit
■Project case1) In case 10mm installation of project thermal insulation material
[7 empty] | to be monitored |  |  | to be monitored |  |  | to be monitored
[7 empty] | ¯ |  |  | ¯ |  |  | ¯
Line Number of main steam pipe linage | Outside diameter of the existing pipe | Thickness covered by the existing thermal insulation material | Thickness installeded by the project thermal insulation material | Length installed by the project thermal insulation material | Surface area covered by existing insulation material | Surface area covered by project thermal insulation material | Total area where project thermal insulation materials have stripped | Reference radiating surface area | Project radiating surface area | Steam flow hours | Reference radiation heat quantity | Thermal insulation efficiency by the project thermal insulation material | Decreasing rate of thermal insulation efficiency by the project thermal insulation material | Project radiation heat quantity | Referencetotal radiationheat quantity | Project total radiation heat quantity
| d(n)ExtP | t(n)ExtI | t(n)PJI | l(n)PJI | SA(n)ExtI | SA(n)PJI-ins | SA(n)PJI-str,y | SA(n)RE,y | SA(n)PJ,y | OH(n)sf,y | qR(n)RE | f(n)PJI-eff | fPJI-dec,y | qR(n)PJ,y | QR(n)RE,y | QR(n)RE,y
| mm | mm | mm | m | m2 | m2 | m2 | m2 | m2 | hours/y | W/m2 | - | - | W/m2 | GJ/y | GJ/y
n = 1 | 273 | 150 | 10 | 127 | 228.6168 | 236.5965 | 0 | 228.6168 | 236.5965 | 4348 | 647 | 0.22 | 0.1 | 519 | 2315.2854 | 1922.0633 | Reference total radiation heat quantity | QRRE,y | 24803.7425 | GJ/y
n = 2 | 273 | 150 | 10 | 127 | 228.6168 | 236.5965 | 0 | 228.6168 | 236.5965 | 4348 | 647 | 0.22 | 0.1 | 519 | 2315.2854 | 1922.0633 | Boiler efficiency | hboiler | 1 | -
n = 3 | 273 | 150 | 10 | 127 | 228.6168 | 236.5965 | 0 | 228.6168 | 236.5965 | 4348 | 647 | 0.22 | 0.1 | 519 | 2315.2854 | 1922.0633 | CO2 Emission factor of coal | EFCO2,coal | 0.101 | tCO2/GJ
n = 4 | 273 | 150 | 10 | 127 | 228.6168 | 236.5965 | 0 | 228.6168 | 236.5965 | 4348 | 647 | 0.22 | 0.1 | 519 | 2315.2854 | 1922.0633 | Reference emissions | REy | 2505 | tCO2/y
n = 5 | 273 | 150 | 10 | 127 | 228.6168 | 236.5965 | 0 | 228.6168 | 236.5965 | 4348 | 647 | 0.22 | 0.1 | 519 | 2315.2854 | 1922.0633 | Project total radiation heat quantity | QRPJ,y | 20615.5234 | GJ/y
n = 6 | 273 | 150 | 10 | 127 | 228.6168 | 236.5965 | 0 | 228.6168 | 236.5965 | 4348 | 647 | 0.22 | 0.1 | 519 | 2315.2854 | 1922.0633 | Boiler efficiency | hboiler | 1 | -
n = 7 | 273 | 150 | 10 | 127 | 228.6168 | 236.5965 | 0 | 228.6168 | 236.5965 | 4348 | 647 | 0.22 | 0.1 | 519 | 2315.2854 | 1922.0633 | CO2 Emission factor of coal | EFCO2,coal | 0.101 | tCO2/GJ
n = 8 | 159 | 150 | 10 | 43 | 62.0056 | 64.7074 | 0 | 62.0056 | 64.7074 | 6070 | 647 | 0.22 | 0.1 | 519 | 876.6505 | 733.8586 | Project emissions | PEy | 2083 | tCO2/y
n = 9 | 159 | 150 | 10 | 43 | 62.0056 | 64.7074 | 0 | 62.0056 | 64.7074 | 6070 | 647 | 0.22 | 0.1 | 519 | 876.6505 | 733.8586 | GHG emission reductions | ERy | 422 | tCO2e/y
n = 10 | 159 | 150 | 10 | 43 | 62.0056 | 64.7074 | 0 | 62.0056 | 64.7074 | 6070 | 647 | 0.22 | 0.1 | 519 | 876.6505 | 733.8586
n = 11 | 159 | 150 | 10 | 43 | 62.0056 | 64.7074 | 0 | 62.0056 | 64.7074 | 6070 | 647 | 0.22 | 0.1 | 519 | 876.6505 | 733.8586
n = 12 | 273 | 150 | 10 | 200 | 360.0265 | 372.5929 | 0 | 360.0265 | 372.5929 | 6070 | 647 | 0.22 | 0.1 | 519 | 5090.1428 | 4225.646
[7 empty] | Sum | 2208.3668 | 2287.5978 |  |  |  |  | Sum | 24803.7425 | 20615.5234
■Project case2) In case 20mm installation of project thermal insulation material
[7 empty] | to be monitored |  |  | to be monitored |  |  | to be monitored
[7 empty] | ¯ |  |  | ¯ |  |  | ¯
Line Number of main steam pipe linage | Outside diameter of the existing pipe | Thickness covered by the existing thermal insulation material | Thickness installeded by the project thermal insulation material | Length installed by the project thermal insulation material | Surface area covered by existing insulation material | Surface area covered by project thermal insulation material | Total area where project thermal insulation materials have stripped | Reference radiating surface area | Project radiating surface area | Steam flow hours | Reference radiation heat quantity | Thermal insulation efficiency by the project thermal insulation material | Decreasing rate of thermal insulation efficiency by the project thermal insulation material | Project radiation heat quantity | Referencetotal radiationheat quantity | Project total radiation heat quantity
| d(n)ExtP | t(n)ExtI | t(n)PJI | l(n)PJI | SA(n)ExtI | SA(n)PJI-ins | SA(n)PJI-str,y | SA(n)RE,y | SA(n)PJ,y | OH(n)sf,y | qR(n)RE | f(n)PJI-eff | fPJI-dec,y | qR(n)PJ,y | QR(n)RE,y | QR(n)RE,y
| mm | mm | mm | m | m2 | m2 | m2 | m2 | m2 | hours/y | W/m2 | - | - | W/m2 | GJ/y | GJ/y
n = 1 | 273 | 150 | 20 | 127 | 228.6168 | 244.5761 | 0 | 228.6168 | 244.5761 | 4348 | 647 | 0.39 | 0.1 | 420 | 2315.2854 | 1607.8865 | Reference total radiation heat quantity | QRRE,y | 24803.7425 | GJ/y
n = 2 | 273 | 150 | 20 | 127 | 228.6168 | 244.5761 | 0 | 228.6168 | 244.5761 | 4348 | 647 | 0.39 | 0.1 | 420 | 2315.2854 | 1607.8865 | Boiler efficiency | hboiler | 1 | -
n = 3 | 273 | 150 | 20 | 127 | 228.6168 | 244.5761 | 0 | 228.6168 | 244.5761 | 4348 | 647 | 0.39 | 0.1 | 420 | 2315.2854 | 1607.8865 | CO2 Emission factor of coal | EFCO2,coal | 0.101 | tCO2/GJ
n = 4 | 273 | 150 | 20 | 127 | 228.6168 | 244.5761 | 0 | 228.6168 | 244.5761 | 4348 | 647 | 0.39 | 0.1 | 420 | 2315.2854 | 1607.8865 | Reference emissions | REy | 2505 | tCO2/y | 10020
n = 5 | 273 | 150 | 20 | 127 | 228.6168 | 244.5761 | 0 | 228.6168 | 244.5761 | 4348 | 647 | 0.39 | 0.1 | 420 | 2315.2854 | 1607.8865 | Project total radiation heat quantity | QRPJ,y | 17264.8174 | GJ/y
n = 6 | 273 | 150 | 20 | 127 | 228.6168 | 244.5761 | 0 | 228.6168 | 244.5761 | 4348 | 647 | 0.39 | 0.1 | 420 | 2315.2854 | 1607.8865 | Boiler efficiency | hboiler | 1 | -
n = 7 | 273 | 150 | 20 | 127 | 228.6168 | 244.5761 | 0 | 228.6168 | 244.5761 | 4348 | 647 | 0.39 | 0.1 | 420 | 2315.2854 | 1607.8865 | CO2 Emission factor of coal | EFCO2,coal | 0.101 | tCO2/GJ
n = 8 | 159 | 150 | 20 | 43 | 62.0056 | 67.4092 | 0 | 62.0056 | 67.4092 | 6070 | 647 | 0.39 | 0.1 | 420 | 876.6505 | 618.6704 | Project emissions | PEy | 1744 | tCO2/y | 6976
n = 9 | 159 | 150 | 20 | 43 | 62.0056 | 67.4092 | 0 | 62.0056 | 67.4092 | 6070 | 647 | 0.39 | 0.1 | 420 | 876.6505 | 618.6704 | GHG emission reductions | ERy | 761 | tCO2e/y | 3044
n = 10 | 159 | 150 | 20 | 43 | 62.0056 | 67.4092 | 0 | 62.0056 | 67.4092 | 6070 | 647 | 0.39 | 0.1 | 420 | 876.6505 | 618.6704
n = 11 | 159 | 150 | 20 | 43 | 62.0056 | 67.4092 | 0 | 62.0056 | 67.4092 | 6070 | 647 | 0.39 | 0.1 | 420 | 876.6505 | 618.6704
n = 12 | 273 | 150 | 20 | 200 | 360.0265 | 385.1593 | 0 | 360.0265 | 385.1593 | 6070 | 647 | 0.39 | 0.1 | 420 | 5090.1428 | 3534.9301
[7 empty] | Sum | 2208.3668 | 2366.8288 |  |  |  |  | Sum | 24803.7425 | 17264.8174
■Project case3) In case 40mm installation of project thermal insulation material
[7 empty] | to be monitored |  |  | to be monitored |  |  | to be monitored
[7 empty] | ¯ |  |  | ¯ |  |  | ¯
Line Number of main steam pipe linage | Outside diameter of the existing pipe | Thickness covered by the existing thermal insulation material | Thickness installeded by the project thermal insulation material | Length installed by the project thermal insulation material | Surface area covered by existing insulation material | Surface area covered by project thermal insulation material | Total area where project thermal insulation materials have stripped | Reference radiating surface area | Project radiating surface area | Steam flow hours | Reference radiation heat quantity | Thermal insulation efficiency by the project thermal insulation material | Decreasing rate of thermal insulation efficiency by the project thermal insulation material | Project radiation heat quantity | Referencetotal radiation heat quantity | Project total radiation heat quantity
| d(n)ExtP | t(n)ExtI | t(n)PJI | l(n)PJI | SA(n)ExtI | SA(n)PJI-ins | SA(n)PJI-str,y | SA(n)RE,y | SA(n)PJ,y | OH(n)sf,y | qR(n)RE | f(n)PJI-eff | fPJI-dec,y | qR(n)PJ,y | QR(n)RE,y | QR(n)RE,y
| mm | mm | mm | m | m2 | m2 | m2 | m2 | m2 | hours/y | W/m2 | - | - | W/m2 | GJ/y | GJ/y
n = 1 | 273 | 150 | 40 | 127 | 228.6168 | 260.5354 | 0 | 228.6168 | 260.5354 | 4348 | 647 | 0.63 | 0.1 | 281 | 2315.2854 | 1145.9486 | Reference total radiation heat quantity | QRRE,y | 24803.7425 | GJ/y
n = 2 | 273 | 150 | 40 | 127 | 228.6168 | 260.5354 | 0 | 228.6168 | 260.5354 | 4348 | 647 | 0.63 | 0.1 | 281 | 2315.2854 | 1145.9486 | Boiler efficiency | hboiler | 1 | -
n = 3 | 273 | 150 | 40 | 127 | 228.6168 | 260.5354 | 0 | 228.6168 | 260.5354 | 4348 | 647 | 0.63 | 0.1 | 281 | 2315.2854 | 1145.9486 | CO2 Emission factor of coal | EFCO2,coal | 0.101 | tCO2/GJ
n = 4 | 273 | 150 | 40 | 127 | 228.6168 | 260.5354 | 0 | 228.6168 | 260.5354 | 4348 | 647 | 0.63 | 0.1 | 281 | 2315.2854 | 1145.9486 | Reference emissions | REy | 2505 | tCO2/y
n = 5 | 273 | 150 | 40 | 127 | 228.6168 | 260.5354 | 0 | 228.6168 | 260.5354 | 4348 | 647 | 0.63 | 0.1 | 281 | 2315.2854 | 1145.9486 | Project total radiation heat quantity | QRPJ,y | 12329.4017 | GJ/y
n = 6 | 273 | 150 | 40 | 127 | 228.6168 | 260.5354 | 0 | 228.6168 | 260.5354 | 4348 | 647 | 0.63 | 0.1 | 281 | 2315.2854 | 1145.9486 | Boiler efficiency | hboiler | 1 | -
n = 7 | 273 | 150 | 40 | 127 | 228.6168 | 260.5354 | 0 | 228.6168 | 260.5354 | 4348 | 647 | 0.63 | 0.1 | 281 | 2315.2854 | 1145.9486 | CO2 Emission factor of coal | EFCO2,coal | 0.101 | tCO2/GJ
n = 8 | 159 | 150 | 40 | 43 | 62.0056 | 72.8127 | 0 | 62.0056 | 72.8127 | 6070 | 647 | 0.63 | 0.1 | 281 | 876.6505 | 447.0999 | Project emissions | PEy | 1246 | tCO2/y
n = 9 | 159 | 150 | 40 | 43 | 62.0056 | 72.8127 | 0 | 62.0056 | 72.8127 | 6070 | 647 | 0.63 | 0.1 | 281 | 876.6505 | 447.0999 | GHG emission reductions | ERy | 1259 | tCO2e/y
n = 10 | 159 | 150 | 40 | 43 | 62.0056 | 72.8127 | 0 | 62.0056 | 72.8127 | 6070 | 647 | 0.63 | 0.1 | 281 | 876.6505 | 447.0999
n = 11 | 159 | 150 | 40 | 43 | 62.0056 | 72.8127 | 0 | 62.0056 | 72.8127 | 6070 | 647 | 0.63 | 0.1 | 281 | 876.6505 | 447.0999
n = 12 | 273 | 150 | 40 | 200 | 360.0265 | 410.292 | 0 | 360.0265 | 410.292 | 6070 | 647 | 0.63 | 0.1 | 281 | 5090.1428 | 2519.3619
[7 empty] | Sum | 2208.3668 | 2525.2907 |  |  |  |  | Sum | 24803.7425 | 12329.4017