## PMS(input)
JCM_ID_F_PMS_ver1.0
Joint Crediting Mechanism Proposed Methodology Spreadsheet Form (input sheet) [Attachment to Proposed Methodology Form]
Table 1: Parameters to be monitored ex post
| (a) | (b) | (c) | (d) | (e) | (f) | (g) | (h) | (i) | (j)
| Monitoring point No. | Parameters | Description of data | Estimated Values | Units | Monitoring option | Source of data | Measurement methods and procedures | Monitoring frequency | Other comments
| 1 | EGp,net | Amount of net electricity generated from CHP | 0 | MWh | Option C | Monitored data | Data is measured by measuring equipments - Specification of measuring equipments： 1) Electrical power meter is applied for measurement of electrical power consumption. 2) Meter is certified in compliance with national/international standards on electrical power meter. - Measuring and recording： 1) Measured data is automatically sent to a server where data is recorded and stored. 2) Recorded data is checked its integrity once a month by responsible staff. - Calibration： Monitoring devices are calibrated in line with international standards or manufacturers' specification. | Monthly
| 2 | CGPJ | Amount of chilled water produced by absorption chiller | 0 | Ton | Option C | Monitored data | Data is measured by measuring equipments - Specification of measuring equipments： 1) Electrical power meter is applied for measurement of electrical power consumption. 2) Meter is certified in compliance with national/international standards on electrical power meter. - Measuring and recording： 1) Measured data is automatically sent to a server where data is recorded and stored. 2) Recorded data is checked its integrity once a month by responsible staff. - Calibration： Monitoring devices are calibrated in line with international standards or manufacturers' specification. | Hourly (Accumulate monthly)
| 3 | TCW, PJ, in, l | Average inlet temperature of the chilled water entering the absorption chiller |  | ℃ | Option C | Monitored data | Data is measured by measuring equipments - Specification of measuring equipments： 1) Electrical power meter is applied for measurement of electrical power consumption. 2) Meter is certified in compliance with national/international standards on electrical power meter. - Measuring and recording： 1) Measured data is automatically sent to a server where data is recorded and stored. 2) Recorded data is checked its integrity once a month by responsible staff. - Calibration： Every year after the installation by a qualified agency. | Hourly (Accumulate monthly)
| 4 | TCW, PJ, out,l | Average outlet temperature of the chilled water leaving the absorption chiller |  | ℃ | Option C | Monitored data | Data is measured by measuring equipments - Specification of measuring equipments： 1) Electrical power meter is applied for measurement of electrical power consumption. 2) Meter is certified in compliance with national/international standards on electrical power meter. - Measuring and recording： 1) Measured data is automatically sent to a server where data is recorded and stored. 2) Recorded data is checked its integrity once a month by responsible staff. - Calibration： Monitoring devices are calibrated in line with international standards or manufacturers' specification. | Hourly (Accumulate monthly)
| 5 | FCPJ,p | Natural gas consumption by CHP | 0 | m3 | Option C | Monitored data | Data is measured by measuring equipments - Specification of measuring equipments： 1) Electrical power meter is applied for measurement of electrical power consumption. 2) Meter is certified in compliance with national/international standards on electrical power meter. - Measuring and recording： 1) Measured data is automatically sent to a server where data is recorded and stored. 2) Recorded data is checked its integrity once a month by responsible staff. - Calibration： Monitoring devices are calibrated in line with international standards or manufacturers' specification. | Monthly
| 6 | NCVp | Net calorific value of natural gas consumed by CHP | 0 | MJ/m3 | Option B | Purchase records | - Collecting purchase amount from retailer invoices monthly and inputting to a spreadsheet manually - Project deputy managers double check the input data with invoices every 6 months | Monthly
| 7 | ECaux,i,p | Amount of electricity consumed by auxiliary equipment i of absorption chillar during a given time period p | 0 | MWh | Option C | Monitored data | Data is measured by measuring equipments - Specification of measuring equipments： 1) Electrical power meter is applied for measurement of electrical power consumption. 2) Meter is certified in compliance with national/international standards on electrical power meter. - Measuring and recording： 1) Measured data is automatically sent to a server where data is recorded and stored. 2) Recorded data is checked its integrity once a month by responsible staff. - Calibration： Monitoring devices are calibrated in line with international standards or manufacturers' specification. | Monthly
Table 2: Project-specific parameters to be fixed ex ante
| (a) | (b) |  | (c) | (d) | (e) |  |  | (f)
| Parameters | Description of data |  | Estimated Values | Units | Source of data |  |  | Other comments
| EFgrid | CO2 emission factor for an Indonesian regional grid system, from which electricity is displaced due to the project during a given time period |  | 0.814 | tCO2/MWh | The most recent value available at the time of validation is applied and fixed for the monitoring period thereafter. The data is sourced from “Emission Factors of Electricity Interconnection Systems”, National Committee on Clean Development Mechanism Indonesian DNA for CDM unless otherwise instructed by the Joint Committee.
| COPRE_default | COP of reference centrifugal chiller under the standardizing temperature conditions |  | 5 | - | Comparing the value of the existing centrifugal chiller and the value of AM002's table , higher COP value is used.
| CEF | Default carbon content of natural gas |  | 15.3 | tC/TJ | Referred to 2006 IPCC Guidelines for National Greenhouse Gas Inventories, Volume 2, Table1.4
Table3: Ex-ante estimation of CO2 emission reductions
| CO2 emission reductions |  | Units
| 0 |  | tCO2/p
[Monitoring option]
| Option A | Based on public data which is measured by entities other than the project participants (Data used: publicly recognized data such as statistical data and specifications)
| Option B | Based on the amount of transaction which is measured directly using measuring equipments (Data used: commercial evidence such as invoices)
| Option C | Based on the actual measurement using measuring equipments (Data used: measured values)

## PMS(calc_process)
JCM_ID_F_MPS_ver1.0
Monitoring Plan Sheet (Calculation Process Sheet) [Attachement to Project Design Document]
1. Calculations for emission reductions |  |  |  |  | Fuel type | Value | Units | Parameter
| Emission reductions during the period p |  |  |  |  | 0 | tCO2/p | ERp
2. Selected default values, etc.
| CO2 emission factor for an Indonesian regional grid system |  |  |  | Electricity | 0.814 | tCO2/MWh | EFgrid
| COP of reference chiller under the standard temperature conditions |  |  |  |  | 5 | - | COPRE_default
| Default carbon content of natural gas |  |  |  | Natural Gas | 15.3 | tC/TJ | CEF
3. Calculations for reference emissions
| Reference emissions during the period p |  |  |  |  | 0 | tCO2/p | REp
Reference emissions
|  |  | Amount of net electricity generated from CHP |  | Electricity | 0 | MWh/p | EGp,net
|  |  | Total cooling effect generated by absorption chillers |  |  | 0 | TJ/p | CGPJ
|  |  | COP of reference chiller under the standard temperature conditions |  |  | 5 | - | COPRE_default
|  |  | Amount of chilled water produced by absorption chiller |  |  | 0 | Ton | CWPJ
|  |  | Average inlet temperature of the chilled water entering the absorption chiller |  |  | 0 | °C | TCW, PJ, in, l
|  |  | Average outlet temperature of the chilled water leaving the absorption chiller |  |  | 0 | °C | TCW, PJ, out, l
4. Calculations of the project emissions
| Project emissions during the period p |  |  |  |  | 0 | tCO2/p | PEp
Project emissions
|  |  | Natural gas consumption by CHP |  | Natural Gas | 0 | m3 | ECPJ,p
|  |  | Net calorific value of natural gas consumed by CHP |  | Natural Gas | 0 | MJ/m3 | NCVp
|  |  | Amount of electricity consumed by auxiliary equipment i |  | Electricity | 0 | MWh/p | ECaux, i, p
[List of Default Values]
|  |  |  | COPRE_default (x<300USRt) | 4.92 | -
|  |  |  | COPRE_default (300≦x<450USRt) | 5.33 | -
|  |  |  | COPRE_default (450≦x<500USRt) | 5.59 | -
|  |  |  | COPRE_default (500≦x<700USRt) | 5.85 | -
|  |  |  | COPRE_default (700≦x<1250USRt) | 5.94 | -

## Sheet2
COPRE_default (x<300USRt) | 4.92
COPRE_default (300≦x<450USRt) | 5.33
COPRE_default (450≦x<500USRt) | 5.59
COPRE_default (500≦x<700USRt) | 5.85
COPRE_default (700≦x<1250USRt) | 5.94